| KAVAAI SOVEREIGN ON-PREMISE AI WORKBENCH INDUSTRIAL MAINTENANCE & INTEGRITY DIVISION | AIR-GAP VERIFIED (0 WAN) SECURITY: INTERNAL USE ONLY |
| --- | --- |

ENGINEERING APPROVAL NOTE: Machine 101 Thermal Variance & Operational Fitness

| DOCUMENT REFERENCE: DOC-REF: APPR-2026-M101-042 | DATE / TIME: September 16, 2026 - 19:03:17 UTC+05:30 |
| --- | --- |
| APPROVAL STATUS: CONDITIONAL APPROVAL | EQUIPMENT / UNIT: Industrial Cooling Unit 101 |
| VERIFICATION AUDIT: PASS - 100% Traceable Evidence | CLASSIFICATION: Sovereign Engineering Deliverable |

# 1. Executive Summary

Inspection findings evaluated. Operating temperature of 84.2°C exceeds 80°C warning limit. Conditional approval granted subject to cleaning.

# 2. Key Inspection Findings vs Authoritative Baseline

Empirical sensor metrics and field observations extracted from the scanned inspection report, compared directly against manufacturer operating thresholds and standard operating procedures:

| Parameter / Inspection Point | Measured Value | SOP Baseline Range | Variance / Delta | Compliance State |
| --- | --- | --- | --- | --- |
| Core Temperature | 84.2°C | 60°C - 80°C | +4.2°C | WARNING (>80°C) |
| Ventilation Fan | 1240 RPM | 1200 - 1400 RPM | Nominal | COMPLIANT |

# 3. Evidence Traceability Matrix

Every claim in this evaluation is mapped to verifiable evidence extracted from scanned files, live telemetry logs, or local knowledge repositories. Zero claims are inferred without direct citation:

| Evidence Source | Modality | Empirical Observation / Fact | Citation Identifier |
| --- | --- | --- | --- |
| Field Inspection Report (IR-2026-0914-A) | DIGITAL_TEXT / OCR | Core temp measured at 84.2°C. | [IR-2026-0914-A: Sec 2] |
| Visual Inspection by R. Sharma | PHYSICAL_OBSERVATION | 20-30% radiator fin dust coverage. | [IR-2026-0914-A: Sec 3] |

# 4. Relevant SOP & Governance Standard References

• SOP-042-REV-3: Thermal Protocol
  Applicability / Section: Sec 2 & 3
  Mandatory Clause: Warning >80°C activates Phase 1 fan inspection & radiator cleaning.

# 5. Recommended Actions & Engineering Protocols

5.1 Grant CONDITIONAL APPROVAL for continued operation for up to 48 hours.

5.2 Clean radiator fins with compressed air within 48 hours.

# 6. Engineering Assumptions & Limitations

— Assumes ambient plant temperature remains <= 32°C.

— Valid exclusively for Machine 101 (ICU-101-A).

# 7. Engineering Sign-Off & Official Determination

| DETERMINATION: CONDITIONAL APPROVAL | AUTHORITY: Chief Maintenance Engineer / Sovereign Plant Authority |
| --- | --- |
| EVALUATION AGENT: KAVAAI Sovereign Autonomous Orchestrator | EXECUTION TOPOLOGY: 100% On-Premise Air-Gapped Loopback |
| AUDIT SIGNATURE: SOVEREIGN-DIGITAL-HASH-VERIFIED | VERIFICATION DATE: September 16, 2026 - 19:03:17 UTC+05:30 |
| APPROVAL CONDITIONS: Mandatory Radiator Cleaning within 48h; Continuous Telemetry Tracking. | NEXT INSPECTION: Within 72 Hours |